COMMERCIAL KITCHEN EXHAUST SHOP STANDARD SUBMITTAL

ACM JOB#

| Proj. Name: |  |
| --- | --- |
| Location: |  |
| Engineer: |  |
| Architect: |  |
| Contractor: |  |
| Date: |  |
| DWG Date: |  |
| REV. No: |  |
| REV. No: |  |
| Notes: | THIS IS ALL CITY METAL INTERPRETATION OF PROJECT SPECIFICATIONS AND DETAILS. PLEASE NOTE ANY DISCREPANCIES. APPROVAL OF THESE STANDARDS IS AN ACKNOWLEDGEMENT OF AGREEMENT WITHIN. |

Project Specific Notes:

| No. | Notes: | Spec Section |
| --- | --- | --- |
| 1 | All ductwork as per SMACNA Standards 4th edition 2020 |  |
| 2 | Commercial Kitchen Hoods: Comply with NFPA96 - Exposed to View to be Stainless Steel Type 304 - Concealed to be Carbon-Steel Sheet (Black Iron) - Welded Seams & Joints - Pressure Class: Positive or Negative 3” wg - Airtight/Watertight |  |
| 3 | NFPA States: 506.3.1 Duct Materials - Ducts servicing Type I hoods shall be constructed of materials in accordance with Sections 506.3.1.1 & 506.3.1.2 |  |
| 4 | Grease Duct Materials – Grease ducts serving Type I hoods and located within buildings shall be constructed as follows: - Duct with a cross-sectional area up to and including 155 square inches (1.0 square meters) shall be constructed of 0.0598 inch (1.52 mm) #16ga steel. - Ducts with a cross-sectional area over 155 square inches (100 000 mm2) but not more than 200 square inches (0.129 m2) shall be constructed of 0.074 inch (1.9mm) #14ga steel. - Duct with a cross-sectional area equal to or more than 200 square inches (0.129 m2) shall be constructed of 0.1046 inch (2.66mmm) #12ga steel. |  |
| 5 | If stainless steel is used for ducts of any of the cross-sectional areas listed above, the gauge steel may be increased upwards (resulting in a smaller thickness) by 1 even gauge size. |  |
| 6 | Most common sizes are 20x20 = 400 sq inches = 12ga. carbon steel material and gauge will be used. |  |
| 7 | 506.3.1.2 Makeup Air Ducts - Make up air ducts connecting to or within 18 inches (457 mm) of a Type I hood shall be constructed and installed in accordance with Sections 603.1, 603.3, 603.4, 603.9,603.10 and 603.12. Duct insulation installed within 18 inches (457 mm) of a Type I hood shall be noncombustible or shall be listed for the application. |  |
| 8 | Installation: - Install exhaust duct without dips & taps that may hold grease. - Sloped a minimum of 2% to drain grease back to hood. - Install access panel within 10ft of each change of direction (greater than 45*) and at maximum intervals of 20ft in horizontal ducts & at each floor for vertical ducts or as shown on drawings |  |
| 9 | Clean Outs: - Not be closer than 1” from the edge of the duct. - Have opening dimensions of not less than 12x12. - Where such dimensions preclude installation the opening shall not be less than 12 inches on one side and shall be large enough to provide access for cleaning and maintenance. - Located at grease reservoirs. |  |